Solar Power Control system Design Description

M. Ray Johnson

Introduction

In 2017, I purchased a 4400 watt two-phase solar electric system that could generate enough electric power to power my entire household when solar energy is available.  It consists of 12 solar panels, 12 AGM batteries, an inverter, a charge controller for the batteries, and a system controller.  Unlike the more typical solar systems currently being installed which simply generate power to be sold back to the utility company, this system is designed to provide household power even in the event of a grid power failure.

Because the delivered system did not give me sufficient control to avoid a lot of on-going human interaction to operate the system, I elected to design a Controller as a ‘front end’ to the system.

The Controller is designed to connect the optimal number of electrical load groups to run on solar power, without unduly discharging the battery bank.  When solar energy is not available (e.g., night time) all loads are normally connected to grid power and, if necessary, the batteries are recharged from grid power.

The system is shown in the Load Shedding Design Diagram.

Five relays, R1 through R5, switch their respective two-phase loads between solar and grid power.  Relays G1 and G2 are used to remove grid power from the load group relays for a fraction of a second when they are being toggled.  This prevents the possibility of creating an arc between solar and grid power.

The inverter is programmed in a mode called Auto Connect.  When grid power is available at the inverter input, inversion ceases and the inverter is bypassed, powering any solar loads directly from the grid.  Thus, relay IV controls the presence or absence of grid voltage at the inverter input.  All eight relays are controlled by the Controller.

Inputs to the Controller consist of the following measurements:

- Grid Voltage, to sense grid power failures

- Battery Voltage, to sense the battery condition

- Battery Current, to sense if the battery is being charged or discharged

- Available solar energy, as measured by a pyranometer.

The Grid/Generator Transfer Switch provides for using a gas-driven generator for short periods of time in the event of a prolonged grid power failure.  When Generator power is being used, the controller interprets it as Grid Power.

The controller is implemented by an Arduino MEGA2560 microcomputer programmed in a C++ like language.  It consists of the MEGA2560, a 40 character by 4-line LCD display, three push buttons, and on/off switch, and all the necessary signal conditioning and interface circuitry.

Six different LCD screens are available to the user.  In the MAN screen, the eight relays are directly controlled.  This MANual mode is intended only for handling problem conditions that could occur.  The AUTO screen displays the load groups currently being powered by solar.  The intent is that the controller will remain in this mode without human intervention for very long periods of time (months).  It is designed to handle the presence or absence of grid power, low battery conditions, etc., without human intervention.

The other screens are the CONDition screen in which current system conditions are displayed, the HISTory screen showing the number of load groups that have  been connected to solar during the last 10 hours, the SHUTDOWN screen that provides a well-behaved shutdown procedure, and the MODE screen which allows the user to switch between different screens.

There is a timer running in the background which interrupts the loop code every minute.  If any major changes in the system state have occurred since the last interrupt, appropriate action is taken.  Every 15 minutes, the solar conditions are re-evaluated and an additional load group is placed on solar power if sufficient solar power is available, one load group is removed and placed on grid power if not, or the load is left unchanged.

Controller Operation

Operating the Controller is done via three pushbutton switches.  These pushbuttons create hardware interrupts; thus the loop code consists of continually checking for interrupt flags and taking appropriate actions.

The MODE button allows the user access to all of the available screens.

The INCrement button allows the user to choose between the various options shown on the current screen.  For example, in the MODE screen, the user chooses which other screen is desired.  In the MAN screen the user chooses which relay he wishes to toggle.

The SELect button allows the user to select the choice made via the INC button.

This simplicity of operation comes at a cost.  The software which implements all the various possibilities of pushbutton combinations is quite involved and requires about 800 lines of C++ code.

AutoMode

The AUTO mode is where the controller is intended to operate essentially all the time, without interruption, without regard to variations in operating conditions.  It is designed to operate in a variety of conditions.  The three basic system parameters are

- The presence or absence of Grid Power.

- The presence or absence of Solar Energy.

- The battery voltage condition, whether above or below desired levels.

Every 15 minutes the autoMode routine is executed.  If solar is available, the controller decides whether to add or remove a load group from Solar, or to leave the load as is, based on whether the batteries are currently being charged or discharged.  That way, the use of solar power is maximized without needlessly discharging the batteries.

Every minute, system conditions are examined to see if any of the three basic system parameters have changed.  If so, autoMode is executed and the 15-minute cycle clock is reset.

The action of AUTO is described in the following table which includes all possible combinations of the system parameters.

| System Parameter Conditions | autoMode Actions. |
| --- | --- |
| Grid and Solar Power are present; Battery voltage is acceptably high. | This is a typical daytime condition in which autoMode would continually maximize the use of available Solar energy. |
| Grid and Solar Power are present; Battery voltage is below the minimum. | This is a very unlikely condition, but if it occurs, all load groups are placed on Grid power, and Grid power is used to recharge the battery. |
| Grid Power is present, Solar is not; Battery voltage is acceptably high. | This is a typical nighttime condition. All load groups are placed on Grid Power and the battery is charged (if necessary) using Grid Power. |
| Grid Power is present, Solar is not; Battery voltage is below the minimum. | This is a very unlikely condition, but if it occurs, all load groups are placed on Grid power, and Grid Power is used to recharge the battery. |
| Grid Power is not present, Solar Power is. Battery voltage is acceptably high. | autoMode would continually maximize the use of available Solar energy. Load groups not connected to Solar are without power. |
| Grid Power is not present, Solar Power is. Battery voltage is below the minimum. | This is a very unlikely condition, but if it occurs, all load groups are placed on Grid power (which means all loads are without power), and available Solar Power is used to recharge the battery. |
| Neither Grid or Solar Power are present; Battery voltage is acceptably high. | In these conditions, Load Groups 1 and 2 (the most crucial in the household) are placed on Solar, which means they are provided power drawn from the battery. |
| Neither Grid or Solar Power are present; Battery voltage is below the minimum. | Without Grid or Solar Power, and with the batteries fading, all load groups are removed from Solar meaning that all load groups are without power. This condition would suggest the use of the gas power generator. When the generator is connected and functioning, the controller cannot distinguish between generator power and Grid Power. |

Software Flowcharts

C++ Code

//This sketch implements the software-based, LCD version of the solar controller.

//Written by M. Ray Johnson, Beginning August 2018 until April 2019.  This algorithm assumes the Inverter is

//placed in the AUTO CONNECT mode.

//UPDATES:

//18March2019: Eliminated all unnecessary relay closures and increased the cycle time to 15 minutes to increase

//relay life.

#include <TimerOne.h>

#include <LiquidCrystal.h>                                          //set up the LCD

const int RS=12, E1=11, E2=10, D4=7, D5=6, D6=5, D7=4;

LiquidCrystal lcd1(RS, E1, D4, D5, D6, D7);               //top two lines of display

LiquidCrystal lcd2(RS, E2, D4, D5, D6, D7);               //bottom two lines of display

volatile boolean incFlag = LOW;                                 //declare variables used in ISRs

volatile boolean selFlag = LOW;

volatile boolean modeFlag = LOW;

volatile boolean timerFlag = LOW;

volatile boolean currentSolarState = LOW;

volatile boolean currentGridState = LOW;

volatile boolean currentBatState = LOW;

volatile boolean changeFlag = LOW;

volatile boolean cycleFlag = LOW;                              //LOW indicates vB has dropped to vBminLow;

volatile boolean vBflag = HIGH;                                   //HIGH indicates vB has risen to vBminHigh.

volatile boolean oldSolarState = LOW;

volatile boolean oldGridState = LOW;

volatile boolean oldBatState = LOW;

volatile boolean incEnable = LOW;                             //LOW disables inc button interrupts

volatile boolean selEnable = LOW;

volatile boolean timerEnable = LOW;

volatile boolean relayState[] = {HIGH, HIGH, HIGH, HIGH, HIGH, HIGH, HIGH, HIGH};  //HIGH indicates de-energized.

//For the LG relays, HIGH indicates the load is

volatile byte manCursorPos = 0;                                 //connected to GRID power; LOW to SOLAR power.

volatile byte index = 0;                                                 //For G1 and G2, HIGH indicates a closed condition,

volatile byte mode = 0;                                                //connecting their respective LGs to GRID.  For

volatile byte horizCursorPos = 0;                               //the IV relay, HIGH indicates a closed condition,

volatile byte solarLoadCount = 0;                              //connecting Grid power to the inverter input.

volatile byte loadStateHistory[] = {0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0};

volatile byte controlState = 0;

volatile byte manIndex = 0;

volatile int powerSources = 0;

volatile int minutes = 0;

volatile int sixSec = 0;

int iBint = 0;

int vBint = 0;

volatile float iB = 0.0;

volatile float pyra = 0.0;

volatile float vB = 0.0;

volatile float vG = 0.0;

volatile int vDir = 0;

volatile int iDir = 1;

volatile unsigned int eventTime = 0;

const float pyraMin = 0.4;

const float vGmin = 100.0;

const float vBminHigh = 53.0;

const float vBminLow = 48.0;

String man1 = "MANUAL MODE";                                          //LCD screen string arrays

String man2 = "Control load group relays as desired";

String man3 = "LG1  LG2  LG3  LG4  LG5  G1   G2   IV   ";

String man4 = "                           ";

String man6 = "All loads on Grid Power        ";

String man7 = "IV cannot open until all LGs are on GRID";

String man10 = "All loads are without power";                    //manSelect are relay state labels

String manSelect[] = {"GRID ","GRID ","GRID ","GRID ","GRID ", "CLO  ", "CLO  ", "CLO  "};

String mode1 = "MODE SELECT";

String mode2 = "Select one of the following modes";

String mode3 = "MAN    AUTO   COND   HIST   SHUTDWN";

String auto1 = "AUTO MODE";

String auto3 = "Grid and Solar Power are available      ";

String auto4 = "Grid Power failure; Solar is available  ";

String auto5 = "Grid Power is available; Solar is not   ";

String auto6 = "Grid Power failure; Solar not available ";

String auto7 = "Load Group(s) on Solar:  ";

String auto15 = "Battery Low";

String menu5 = "CURRENT CONDITIONS";

String shutdwn1 = "PLEASE WAIT";

String shutdwn2 = "PLEASE TURN THE CONTROLLER OFF NOW";

String history1 = "SOLAR LOAD HISTORY";

const byte relay1 = 22;                //Load Group 1 relay LOW is SOLAR (energized)

const byte relay2 = 23;                //Load Group 2 relay

const byte relay3 = 24;                //Load Group 3 relay

const byte relay4 = 25;                //Load Group 4 relay

const byte relay5 = 26;                //Load Group 5 relay

const byte relayG1 = 27;             //Grid relay for Load Groups 1,2.  LOW is open (energized)

const byte relayG2 = 28;             //Grid relay for Load Groups 3,4,5.  LOW is open (energized)

const byte relayIv = 29;               //Inverter Input relay.  LOW is open (energized)

const byte batCurrent = A10;     //Battery Current 0 to 1023 counts = -25 to +25 amps.  Was A4

const byte pyranometer = A7;   //0 to 5.0 VDC signal.  Was A0

const byte batVoltage = A8;       //0 to 66.7 VDC.  Was A2

const byte gridVoltage = A9;      //5.12 VDC corresponds to 125 VAC (RMS).  Was A3

const int arcDelayPeriod = 20;   //current arc delay period in ms

//Analog input A1 is apparently faulty.  Move all analog

//inputs to A7 thru A10

void setup() {

Serial.begin(9600);                     //enable the computer serial monitor

lcd1.begin(40,2);                        // set up the LCD's number of columns and rows:

lcd2.begin(40,2);

pinMode(4, OUTPUT);               //Define digital I/O, LCD data and control lines

pinMode(5, OUTPUT);

pinMode(6, OUTPUT);

pinMode(7, OUTPUT);

pinMode(11, OUTPUT);

pinMode(10, OUTPUT);

pinMode(12, OUTPUT);

pinMode(relay1, OUTPUT);             //Relay control lines - Load Group 1 Relay

pinMode(relay2, OUTPUT);             //LG2 Relay

pinMode(relay3, OUTPUT);             //LG3 Relay

pinMode(relay4, OUTPUT);             //LG4 Relay

pinMode(relay5, OUTPUT);             //LG5 Relay

pinMode(relayG1, OUTPUT);          //G1 Relay

pinMode(relayG2, OUTPUT);          //G2 Relay

pinMode(relayIv, OUTPUT);            //IV Relay

pinMode(pyranometer, INPUT);    //Define analog inputs. 0 to 5.0 VDC signal

pinMode(gridVoltage, INPUT);       //0 to 125 VAC (RMS)

pinMode(batVoltage, INPUT);        //0 to 60 VDC

pinMode(batCurrent, INPUT);         //-25 to +25 amps

attachInterrupt(digitalPinToInterrupt(2), isrMode, RISING);          //set up 1st priority interrupt (Mode, on pin 2)

attachInterrupt(digitalPinToInterrupt(3), isrIncrement, RISING);  //set up 2nd priority interrupt (Inc, on pin 3)

attachInterrupt(digitalPinToInterrupt(18), isrSelect, RISING);       //set up 3rd priority interrupt (Select, on pin 18)

Timer1.initialize(6000000);                                                                  //set up 4th priority interrupt (Timer, every 6 sec)

Timer1.attachInterrupt(isrTimer);

modeScreen();                                     //launch the mode screen

digitalWrite(relayG1, LOW);             //open G1

digitalWrite(relayG2, LOW);             //open G2

delay(arcDelayPeriod);

digitalWrite(relayIv, HIGH);              //close IV

relayState[7] = HIGH;

manSelect[7] = "CLO  ";

for(byte i = 0; i < 5; i++) {                   //de-energize all Load Group relays [This leaves all Load Group Relays

digitalWrite(22 + i, HIGH);               //in the GRID position, and G1, G2, and IV closed.

relayState[i] = HIGH;

manSelect[i] = "GRID ";}

delay(arcDelayPeriod);

digitalWrite(relayG1, HIGH);             //close G1

relayState[5] = HIGH;

manSelect[5] = "CLO  ";

digitalWrite(relayG2, HIGH);            //close G2

relayState[6] = HIGH;

manSelect[6] = "CLO  ";

modeFlag = LOW;                               //reset all the interrupt flags

incFlag = LOW;

selFlag = LOW;

timerFlag = LOW;

cycleFlag = LOW;

solarLoadCount = 0;

index = 0;

manIndex = 0;

horizCursorPos = 0;

manCursorPos = 0;

checkStateChange();                           //initialize the change state conditions

oldSolarState = currentSolarState;

oldGridState = currentGridState;

oldBatState = currentBatState;

changeFlag = LOW;

vBflag = HIGH;

minutes = 0;

for(int i = 0; i < 40; i++) {                 //initialize history

loadStateHistory[i] = 0;}

controlState = 0; }                           //end of setup

void loop() {

if(modeFlag == HIGH) {                  //check to see if Mode Button has been pressed

delay(300);                                     //debounce

modeFlag = LOW;

if(mode == 0) {                               //if I'm in mode screen

controlState = 0;

modeScreen();

return;}

else if(mode == 1) {                       //if I'm in man screen

manCursorPos = horizCursorPos;           //save the cursor position

manIndex = index;

modeScreen();

return; }

else if(mode == 2) {                       //if I'm in auto screen

modeScreen();

return; }

else if(controlState == 0) {           //if I'm in no control

modeScreen();

return; }

else if(controlState == 1) {           //if I'm in man control

horizCursorPos = manCursorPos;           //restore the cursor position

index = manIndex;

manMode();

return; }

else {                                               //I'm in auto control

autoMode();

return; } }

else if(incFlag == HIGH) {               //check to see if Increment Button has been pressed

delay(300);                                    //debounce

incFlag = LOW;

if(mode == 0) {                              //if I'm currently in Mode screen

if(horizCursorPos < 28) {           //move the cursor in the Mode screen

horizCursorPos += 7;}

else horizCursorPos = 0;

lcd2.setCursor(horizCursorPos,0);        //reposition the cursor

index = horizCursorPos/7;                      //point to the current menu item

return; }

else {                                              //I'm currently in Man screen

if(horizCursorPos < 35) {          //move the cursor in the Man screen

horizCursorPos += 5;}

else horizCursorPos = 0;

lcd2.setCursor(horizCursorPos,1);        //reposition the cursor

index = horizCursorPos/5;                      //point to current relay

return; } }

else if(selFlag == HIGH) {              //check to see if the Select Button has been pressed

delay(300);                                   //debounce

selFlag = LOW;

if(mode == 0) {                             //if I'm in the mode screen

if(index == 0) {                           //if Man Mode has been selected

horizCursorPos = manCursorPos;         //restore the cursor position

index = manIndex;

manMode();                             //launch manMode

return; }

else if(index == 1) {                    //if Auto Mode has been selected

minutes = 0;                             //start the cycle clock

if(solarLoadCount > 0) {         //adjust IV according to solarLoadCount

if(relayState[7] == HIGH) {   //if IV is closed, open it

relayState[7] = LOW;

manSelect[7] = "OPEN ";

digitalWrite(relayIv, LOW); } }

else {

if(relayState[7] == LOW) {    //if IV is open, close it

relayState[7] = HIGH;

manSelect[7] = "CLO  ";

digitalWrite(relayIv, HIGH); } }

autoMode();                             //launch autoMode

return; }

else if(index == 2) {                    //if Conditions Mode has been selected

conditionsScreen();                 //launch conditionsScreen

return; }

else if(index == 3) {                    //History Mode has been selected

historyScreen();                        //launch history screen

return; }

else {                                            //Shutdown has been selected

shutdwnScreen();                    //launch shutdown screen

return;} }

else {                                             //I'm currently in the Man screen

manToggle();

manCursorPos = horizCursorPos;           //save the cursor position

manIndex = index;

return;} }

else if(timerFlag == HIGH) {        //check timer flag

timerFlag = LOW;

if(sixSec >= 10){

sixSec = 0;

checkVbFlag();

checkStateChange();

if(mode == 4) conditionsScreen();

if(mode == 5) historyScreen();

if(changeFlag == HIGH) {         //if the system state has changed

Serial.print("State change detected.  Time = ");

eventTime = millis()/60000;

Serial.println(eventTime);

Serial.print("vB = ");

Serial.println(vB);

Serial.print("pyra = ");

Serial.println(pyra);

Serial.print("vG = ");

Serial.println(vG);

if(mode == 2) goto t1;

else if(mode == 1) {

manMode();

return; }

else return; }

else if(controlState != 2) return;

else {

printCycle();                            //update the cycle display

if(minutes >= 15) {                 //if 15 minutes have passed

t1:       cycleFlag = HIGH;

minutes = 0;

updateHistory();

autoMode();

return; }

else {

minutes ++;

return;} } }

else {

sixSec ++;

return;} }

else return; }                               //end of loop

//*****PUT CALLED FUNCTIONS HERE*****

void modeScreen(void) {               //This function clears the display, then creates the Mode Screen

lcd1.clear();

lcd2.clear();

lcd1.setCursor(0,0);

lcd1.print(mode1);                       //print "MODE SELECT" on LCD line 1

lcd1.setCursor(0,1);

lcd1.print(mode2);                       //print LCD line 2

lcd2.setCursor(0,0);

lcd2.print(mode3);                       //print LCD line 3

lcd2.setCursor(0,0);                     //turn on the blinking cursor

lcd2.cursor();

lcd2.blink();

horizCursorPos = 0;

index = 0;

mode = 0;

selEnable = HIGH;                        //enable select interrupts

incEnable = HIGH;                        //enable increment interrupts

timerEnable = LOW;                    //disable timer interrupts

return; }                                         //end of modeScreen

void conditionsScreen(void) {     //This function clears the dsplay, then creates the

lcd1.clear();                                  //Conditions Screen.

lcd2.clear();

lcd1.noCursor();

lcd1.noBlink();

lcd2.noCursor();

lcd2.noBlink();

lcd1.setCursor(0,0);

lcd1.print(menu5);                       //"CURRENT CONDITIONS"

printConditions();                         //print conditions on LCD lines 2 and 3

readPowerSources();

lcd2.setCursor(0,1);                     //print power sources on line 4

if(powerSources == 3) lcd2.print(auto3); //"Grid and Solar Power are available"

if(powerSources == 2) lcd2.print(auto4); //"Grid Power failure; Solar is available"

if(powerSources == 1) lcd2.print(auto5); //"Grid Power is available; Solar is not"

if(powerSources == 0) lcd2.print(auto6); //"Grid Power failure; Solar not available"

selEnable = LOW;                         //disable Select Button interrupts

incEnable = LOW;                         //disable Increment Button interrupts

timerEnable = HIGH;                    //enable timer interrupts

mode = 4;

return; }                                         //end of Conditions Screen

void historyScreen(void) {            //This function clears the display, then creates the

lcd1.clear();                                   //History Screen.

lcd2.clear();

lcd1.setCursor(0,0);

lcd1.print(history1);                    //"SOLAR LOAD HISTORY"  on line 1

lcd1.noCursor();

lcd1.noBlink();

lcd2.noCursor();

lcd2.noBlink();

printHistory();                              //print the load history on LCD line 4

readPowerSources();

lcd2.setCursor(0,1);                    //print power sources on line 4

if(powerSources == 3) lcd2.print(auto3); //"Grid and Solar Power are available"

if(powerSources == 2) lcd2.print(auto4); //"Grid Power failure; Solar is available"

if(powerSources == 1) lcd2.print(auto5); //"Grid Power is available; Solar is not"

if(powerSources == 0) lcd2.print(auto6); //"Grid Power failure; Solar not available"

selEnable = LOW;                         //disable Select Button interrupts

incEnable = LOW;                         //disable Increment Button interrupts

timerEnable = HIGH;                    //enable timer interrupts

mode = 5;

return; }                                         //end of historyScreen

void shutdwnScreen(void) {         //This function provides for a well-behaved

lcd1.clear();                                   //shutdown process that creates the Shutdown

lcd2.clear();                                   //screen, de-energizes all relays, invites the

lcd2.noCursor();                           //user to turn off the controller, and enters

lcd2.noBlink();                              //an endless loop.

boolean b = LOW;                        //avoid unnecessary relay actions

for(int a = 2; a < 5; a++) {

if(relayState[a] == LOW) b = HIGH; }

if(b == HIGH) {

digitalWrite(relayG1, LOW);      //Open G1

delay(arcDelayPeriod);

for(int q = 0; q < 5; q++) {

if(relayState[q] == LOW) {

solarLoadCount--;

digitalWrite(q + 22, HIGH);

relayState[q] = HIGH;

manSelect[q] = "GRID "; } }

delay(arcDelayPeriod);

digitalWrite(relayG1, HIGH); }    //Close G1

digitalWrite(relayIv, HIGH);              //close IV

selEnable = LOW;                               //disable select interrupts

incEnable = LOW;                               //disable increment interrupts

timerEnable = LOW;                          //disable timer interrupts

s1: lcd1.setCursor(0,0);

lcd1.print(shutdwn2);                       //LCD line 1: "PLEASE TURN THE CONTROLLER OFF NOW"

delay(1000);

lcd1.clear();

delay(300);

goto s1;                                               //endless loop

return; }                                              //end of Shutdown Screen

void manMode(void) {                       //This function implements the Manual Mode.  It

mode = 1;                                           //creates the appropriate screen depending on

controlState = 1;                               //conditions.

incEnable = HIGH;                             //enable Increment Interrupts

selEnable = HIGH;                             //enable Select Interrupts

timerEnable = HIGH;                        //enable Timer Interrupts

readPowerSources();

lcd1.clear();

lcd2.clear();

lcd1.setCursor(0,0);

lcd1.print(man1);                             //"MANUAL MODE" on line 1

lcd1.setCursor(0,1);                         //print power sources on line 2

if(powerSources == 3) lcd1.print(auto3);   //"Grid and Solar Power are available"

if(powerSources == 2) lcd1.print(auto4);   //"Grid Power failure; Solar is available"

if(powerSources == 1) lcd1.print(auto5);   //"Grid Power is available; Solar is not"

if(powerSources == 0) lcd1.print(auto6);   //"Grid Power failure; Solar not available"

lcd2.setCursor(0,0);

lcd2.print(man3);                             //"LG1  LG2  LG3  LG4  LG5  G1   G2   IV   "

lcd2.setCursor(0,1);

for(int p = 0; p < 8; p++) {               //print current relay states on line 4

lcd2.print(manSelect[p]); }

lcd2.setCursor(horizCursorPos,1);          //put the cursor back where it was

lcd2.cursor();

lcd2.blink();

checkVbFlag();

if(vBflag == HIGH) {

lcd1.setCursor(28,0);                    //clear the "battery Low" message

lcd1.print("           "); }

else {

lcd1.setCursor(28,0);

lcd1.print(auto15); }                    //Print "Battery Low" message

return; }                                           //end of manMode

void autoMode(void) {                   //This function implements the Auto Mode

Serial.print("AUTO Mode executed.  Time = ");

eventTime = millis()/60000;

Serial.println(eventTime);

incEnable = LOW;                           //disable increment interrupts

selEnable = LOW;                           //disable select interrupts

timerEnable = HIGH;                      //enable timer interrupts, for 5 minute load checks.

checkVbFlag();                                //This function executes every five minutes or

mode = 2;                                        //sooner if gross system conditions change.

controlState = 2;

if(manSelect[5] = "OPEN ") {        //if G1 is open, close it.  This is in case some

relayState[5] = HIGH;                  //idiot left G1 or G2 open when leaving MAN mode.

manSelect[5] = "CLO  ";

digitalWrite(relayG1, HIGH); }

if(manSelect[6] = "OPEN ") {       //if G2 is open, close it.

relayState[6] = HIGH;

manSelect[6] = "CLO  ";

digitalWrite(relayG2, HIGH); }

lcd1.clear();                                    //clear the auto mode Screen

lcd2.clear();

lcd1.setCursor(0,0);

lcd1.print(auto1);                         //print "AUTO MODE" on LCD line 1

horizCursorPos = 0;

lcd2.noCursor();                           //turn off the blinking cursor

readPowerSources();

lcd2.noBlink();

lcd1.setCursor(0,1);                    //print power sources on line 2

if(powerSources == 3) lcd1.print(auto3);   //"Grid and Solar Power are available"

if(powerSources == 2) lcd1.print(auto4);   //"Grid Power failure; Solar is available"

if(powerSources == 1) lcd1.print(auto5);   //"Grid Power is available; Solar is not"

if(powerSources == 0) lcd1.print(auto6);   //"Grid Power failure; Solar not available"

if(vBflag == HIGH) {

lcd2.setCursor(0,1);

lcd2.print(man4);                      //clear the "Battery Low" message

if(powerSources >= 1) {           //if either Grid or Solar power is available

if(cycleFlag == HIGH) {            //if the cycle time is up

cycleFlag = LOW;

if(powerSources >= 2) {        //if solar is available

adjustLoad();

if(solarLoadCount == 0) {

a3:         lcd2.setCursor(0,0);

lcd2.print(man6);               //print "All loads on GRID ..." on LCD line 3

a4:         if(relayState[7] == LOW) {       //close IV

relayState[7] = HIGH;

manSelect[7] = "CLO  ";

digitalWrite(relayIv, HIGH); }

a5:         printCycle();                     //print cycle time

printIv();                              //print IV relay state

return; }

else {

a6:         if(relayState[7] == HIGH) {      //open IV

relayState[7] = LOW;

manSelect[7] = "OPEN ";

digitalWrite(relayIv, LOW); }

a2:           lcd2.setCursor(0,0);

lcd2.print(auto7);             //print LCD line 3

solarLoadCount = 0;         //print the load groups on solar

for (int q = 0; q < 5; q++) {

if(relayState[q] == LOW) {

solarLoadCount++;

lcd2.print(q + 1);

lcd2.print("  "); } }

goto a5; } }

else {                                        //solar power is not available; put all load groups on Grid

a1:       boolean b = LOW;             //avoid unnecessary relay actions

for(int a = 2; a < 5; a++) {

if(relayState[a] == LOW) b = HIGH; }

if(b == HIGH) {

digitalWrite(relayG1, LOW);      //Open G1

delay(arcDelayPeriod);

for(int q = 0; q < 5; q++) {

if(relayState[q] == LOW) {

digitalWrite(q + 22, HIGH);

relayState[q] = HIGH;

manSelect[q] = "GRID "; } }

delay(arcDelayPeriod);

digitalWrite(relayG1, HIGH); }    //Close G1

solarLoadCount = 0;

if(powerSources == 1 || powerSources == 3) goto a3;     //if Grid power is available

else {

lcd2.setCursor(0,0);            //print LCD line 3,  "All loads are without power" message

lcd2.print(man10);

goto a4; } } }

else goto a2; }

else {                                            //put LG 1,2 on Solar; put LG 2,3,4 on Grid

if(relayState[0] == HIGH || relayState[1] == HIGH) {  //avoid unnecessary relay actions

digitalWrite(relayG1, LOW);          //Open G1

delay(arcDelayPeriod);

for(int q = 0; q < 2; q++) {     //connect LG 1 and 2 to Solar

if(relayState[q] == HIGH) {

digitalWrite(q + 22, LOW);

relayState[q] = LOW;

manSelect[q] = "SOL  "; } }

solarLoadCount = 2;

boolean b = LOW;                     //avoid unnecessary relay actions

for(int a = 2; a < 5; a++) {

if(relayState[a] == LOW) b = HIGH; }

if(b == HIGH) {

for(int q = 2; q < 5; q++) {       //connect LG 3, 4, and 5 to Grid

if(relayState[q] == LOW) {

digitalWrite(q + 22, HIGH);

relayState[q] = HIGH;

manSelect[q] = "GRID "; } } }

delay(arcDelayPeriod);

digitalWrite(relayG1, HIGH); }  //Close G1

goto a6; } }

else {

lcd2.setCursor(0,1);

lcd2.print(auto15);                      //Print "Battery Low" on LCD line 4

goto a1; } }                                    //End of autoMode

//This function changes the state of the relay in the MAN display that has been selected for toggle.

//It switches the actual selected relay, and also syncs manSelect[] and RelayState[].  The global

//variable "index" points to the selected relay.   If any of the LG relays are toggled, G1 or G2 will

//be opened momentarily to provide arc protection.  Called only from manMode.

void manToggle(void) {

if(index < 2) {                                  //if the selected relay is LG1 or LG2

if(manSelect[5] == "CLO  ") {      //if G1 is closed, open it

digitalWrite(relayG1, LOW);

delay(arcDelayPeriod);}

relayToggle();                                //Toggle the relay

delay(arcDelayPeriod);

digitalWrite(relayG1, HIGH);      //close G1

goto m1; }

else if(index < 5) {                           //if the selected relay is LG3, LG4, or LG5

if(manSelect[6] == "CLO  ") {      //if G2 is closed, open it

digitalWrite(relayG2, LOW);

delay(arcDelayPeriod);}

relayToggle();                               //Toggle the relay

delay(arcDelayPeriod);

digitalWrite(relayG2, HIGH);     //close G2

goto m1; }

else ctrlToggle();                            //if the selected relay is G1, G2, or IV, toggle it

m1: lcd2.setCursor(0,0);

lcd2.print(man3);                          //reprint LCD line 3

lcd2.setCursor(0,1);

for(int p = 0; p < 8; p++) {             //print current relay states on line 4

lcd2.print(manSelect[p]); }

lcd2.setCursor(horizCursorPos,1);           //put the cursor back where it was

return; }                                          //end of manToggle

void relayToggle(void) {                          //This function toggles the state of the load relays, LG1

if(manSelect[index] == "GRID ") {        //through LG5, pointed to by the global pointer 'index'.

manSelect[index] = "SOL  ";               //manSelect, relayState and the actual relay are kept in sync.

relayState[index] = LOW;                   //It is called only from manToggle.  This function DOES NOT

digitalWrite((22 + index), LOW);       //provide arc protection which must be done in the calling

solarLoadCount++; }                           //function.  solarLoadCount is also adjusted as needed.

else {

manSelect[index] = "GRID ";

relayState[index] = HIGH;

digitalWrite((22 + index), HIGH);

solarLoadCount--; }

return; }                                                  //end of relayToggle

void ctrlToggle(void) {                           //This function toggles the state of the control relay G1,

if(index > 6) {                                        //G2 or IV, pointed to by the global pointer 'index'.

if(manSelect[7] == "OPEN ") {         //manSelect, relayState and the actual relay are kept in

manSelect[7] = "CLO  ";                  //sync.  It is called only from manToggle.

relayState[7] = HIGH;

digitalWrite(relayIv, HIGH); }

else {

manSelect[7] = "OPEN ";

relayState[7] = LOW;

digitalWrite(relayIv, LOW); }

return; }

else if(manSelect[index] == "CLO  ") {           //Toggle either G1 or G2 pointed to by 'index'

manSelect[index] = "OPEN ";

relayState[index] = LOW;

digitalWrite((22 + index), LOW); }

else {

manSelect[index] = "CLO  ";

relayState[index] = HIGH;

digitalWrite((22 + index), HIGH); }

return; }                                              //end of ctrlToggle

void readPowerSources() {                                 //This function identifies the current power

measureVg();                                                       //sources (Grid and Solar) eturns the global

measureSolar();                                                  //variable powerSources as follows:

if(vG > vGmin && pyra >= pyraMin) powerSources = 3;      //0 = no power, 1 = grid power only,

else if(vG >= vGmin && pyra < pyraMin) powerSources = 1; //2 = solar power only, 3 = both grid and solar.

else if(vG < vGmin && pyra >= pyraMin) powerSources = 2;

else powerSources = 0;

return; }                                                               //end of readPowerSource

void adjustLoad(void) {                        //This function adjusts the number of load groups

measureIb();                                        //connected to solar power.  It is called only from

if(iB > 0.0) {                                          //function autoMode.  Global variable solarLoadCount

if(solarLoadCount >= 5) return;     //contains the number of load groups currently

else {                                                   //connected to solar power.  Basis for the load

increaseLoad();                               //adjustment is whether or not battery current is

return; } }                                         //positive.  If so, an attempt is made to add an

else if(solarLoadCount == 0) return;         //additional Load Group to solar power.  If not,

else {                                                    //a Load Group is removed.

decreaseLoad();

return; } }                                          //end of adjustLoad

void increaseLoad(void) {                 //This function attempts to add an additional load group to

int i = -1;                                            //Solar power.  Loads are always added from relay1 to relay5.

c1:  i++;                                               //If solarLoadCount becomes greater than zero, IV is opened.

if(i > 4) return;                                 //if all load groups have been tried

if(relayState[i] == LOW) goto c1   //if this LG relay is already connected to solar

if(i < 2) {

digitalWrite(relayG1, LOW);        //Open G1

delay(arcDelayPeriod);

digitalWrite(i + 22, LOW);            //add one load group to solar, relay1 or relay2

delay(arcDelayPeriod);

digitalWrite(relayG1, HIGH); }    //Close G1

else {

digitalWrite(relayG2, LOW);        //Open G2

delay(arcDelayPeriod);

digitalWrite(i + 22, LOW);            //add one load group to solar, relay3, relay4, or relay5

delay(arcDelayPeriod);

digitalWrite(relayG2, HIGH); }     //Close G2

manSelect[i] = "SOL  ";

relayState[i] = LOW;

solarLoadCount ++;

if(relayState[7] == HIGH) {            //if IV is closed, open it

relayState[7] = LOW;

manSelect[7] = "OPEN ";

digitalWrite(relayIv, LOW); }

return; }                                           //end of increaseLoad

void decreaseLoad(void) {                //This function disconnects one load group from solar.

int i = 5;                                              //Loads are always deleted from relay5 to relay1.  If

b1: i--;                                                   //solarLoadCount goes to zero, IV is closed.

if(i < 0) return;

if(relayState[i] == HIGH) goto b1;

if(i < 2) {

digitalWrite(relayG1, LOW);         //Open G1

delay(arcDelayPeriod);

digitalWrite(i + 22, HIGH);             //remove one load group from solar power, relay1 or relay2

delay(arcDelayPeriod);

digitalWrite(relayG1, HIGH); }       //Close G1

else {

digitalWrite(relayG2, LOW);          //Open G2

delay(arcDelayPeriod);

digitalWrite(i + 22, HIGH);              //remove one load group from solar power, relay3, relay4, or relay5

delay(arcDelayPeriod);

digitalWrite(relayG2, HIGH); }       //Close G2

delay(arcDelayPeriod);

manSelect[i] = "GRID ";                     //keep manSelect up to date

relayState[i] = HIGH;                          //keep relayState up to date

solarLoadCount --;

if(solarLoadCount == 0) {                   //if all loads have been connected to Grid power

if(relayState[7] == LOW) {               //if IV is open, close it

relayState[7] = HIGH;

manSelect[7] = "CLO  ";

digitalWrite(relayIv, HIGH); }

return; }

else return; }                                       //end of decreaseLoad

void updateHistory(void) {                        //This function updates the load history array

for(byte m = 39; m > 0 ; m--) {                //adding the latest value on the left and shifting

loadStateHistory[m] = loadStateHistory[m-1]; } //previous values to the right, retaining only the

loadStateHistory[0] = solarLoadCount;                  //latest 40 values (about 3 hours worth).

}                                                                     //end of updateHistory

void printHistory(void) {                           //this function updates solar connection history on

lcd1.setCursor(0,1);                                 //LCD line 2

for(byte z  = 0; z < 40; z++) {

lcd1.print(loadStateHistory[z]); }

return; }                                                     //end of printHistory

void printCycle(void) {                             //This function prints the cycle time (min:sec) at

lcd1.setCursor(29,0);                             //the end of LCD line 1.

lcd1.print("cycle ");

lcd1.print(minutes);

return; }                                                   //end of printCycle

void printIv(void) {                                  //This function prints the state of the IV relay on

lcd2.setCursor(27,1);                            //the end of LCD line 4.

lcd2.print("            ");

lcd2.setCursor(27,1);

lcd2.print("IVR = ");

if(relayState[7] == HIGH) lcd2.print("CLOSED");

else lcd2.print("OPEN");

return;}                                                 //end of printIv

void measureVg(void) {                       //This function measures Grid Voltage

int vGint = 0;                                        //Take 5 readings and average them

for(int w = 0; w < 5; w++) {

vGint = analogRead(gridVoltage) + vGint;

delay(1);}

vG = float(vGint/31.10);                    //Gives value in VAC

return; }

void measureSolar(void) {                   //This function measures solar power availability

int pyraInt = 0;                                     //Take 5 readings and average them

for(int x = 0; x < 5; x++) {

pyraInt = analogRead(pyranometer) + pyraInt;

delay(1);}

pyra = float(pyraInt)/1023.0;

//pyra = 1.0;

return; }

void measureVb(void) {                       //This function measures battery voltage

vBint = 0;                                              //Take 5 readings and average them

for(int y = 0; y < 5; y++) {

vBint = analogRead(batVoltage) + vBint;

delay(1);}

vB = float(vBint)/85.2;

/*if(vDir == 1) {                                   //for test purposes

vB = vB + 0.3;

if(vB > 54.0) vDir = 0; }

else {

vB = vB - 0.3;

if(vB < 46.0) vDir = 1; }*/

return; }

void measureIb(void) {                       //Range is roughly -25 amp to +25 amps over the range

iBint = 0;                                              //Take 5 readings and average them.  This is a very

for(int z = 0; z < 5; z++) {                   //noisy meassurement.

iBint = analogRead(batCurrent) + iBint;

delay(1); }

iBint = iBint/5;                                    //0 to 1023.  So zero current is about 512.

iBint = iBint - 512;                              //get to zero offset

iB = float(iBint) * 0.048828;             //convert counts to amps

iB = (0.741 * iB) - 3.244;                   //conform to test data.  The offset was

//iB = 1.0;                                            //originally -4.444.  I'm varying it to find

/*if(iBflag == 1) {

iB = iB + 0.2;

if(iB >= 1.0) iBflag = 0; }

else {

iB = iB - 0.2;

if(iB <= -1.0) iBflag = 1; }

Serial.print("iB = ");

Serial.println (iB);*/

return; }                                              //the best balance.

void checkVbFlag(void) {                   //This function changes vBflag depending on the

measureVb();                                    //history of vB.

if(vB >= vBminHigh) vBflag = HIGH;

else if(vB < vBminLow) vBflag = LOW;

else return; }

void checkStateChange(void) {        //this function checks the gross system state

measureSolar();                                //(presence of solar, grid voltage, and high battery

checkVbFlag();                                  //voltage) and compares them with values last measured.

measureVg();                                    //If a major change has occured, changeFlag is set HIGH

if(pyra > pyraMin) currentSolarState = HIGH; //and the current LCD screen is updated to reflect these

else currentSolarState = LOW;                           //depending on the current mode.  It is called only from

if(vG > vGmin) currentGridState = HIGH;         //the code that services the timer ISR, and is typically

else currentGridState = LOW;                            //executed every minute if the timer interrupt is enabled.

if(vBflag == HIGH) currentBatState = HIGH;

else currentBatState = LOW;

changeFlag = LOW;

if(currentSolarState != oldSolarState) {

changeFlag = HIGH;

oldSolarState = currentSolarState; }

if(currentGridState != oldGridState) {

changeFlag = HIGH;

oldGridState = currentGridState; }

if(currentBatState != oldBatState) {

changeFlag = HIGH;

oldBatState = currentBatState; }

return; }                                           //end of checkStateChange

void printConditions(void) {           //this function measures current conditions and

measureVg();                                  //prints them on LCD lines 2 and 3

measureSolar();

measureVb();

measureIb();

lcd1.setCursor(0,1);

lcd1.print("Vg = ");

lcd1.print(vG,1);

lcd1.print("    Vb = ");

lcd1.print(vB,1);

lcd1.print("    IVR = ");

if(relayState[7] == HIGH) lcd1.print("CLOSED");

else lcd1.print("OPEN  ");

lcd2.setCursor(0,0);

lcd2.print("Pyra = ");

lcd2.print(pyra,2);

lcd2.print("    Ib = ");

lcd2.print(iB,1);

return; }                                        //end of printConditions

//*****PUT ISRs HERE*****

void isrMode(void) {                 //first priority ISR - Mode Button, never disabled

modeFlag = HIGH; }

void isrIncrement(void) {         //second priority ISR - Increment Button

incFlag = incEnable; }              //raise the interrupt flag if it is enabled

void isrSelect(void) {                //third priority ISR - Select Button

selFlag = selEnable; }              //raise the interrupt flag if it is enabled

void isrTimer(void) {                 //fourth priority ISR - Timer

timerFlag = timerEnable; }     //raise the timer flag if it is enabled

Pictures

The first picture shows the entire solar panel including the solar panel charge controller on the right, the inverter and associated equipment in the center, and my front-end controller on the left.

The next picture is a close-up of the controller showing the AUTO mode screen.  Look closely and you will see that 4 of the 5 load groups are currently being powered by solar.

The third picture shows my modified breaker panel.  The large panel near the center is the original main panel.  The five smaller panels are the individual breaker panels for the five load groups.  The blank panels house boxes containing the power transfer relays that would otherwise not fit in the smaller breaker panel boxes.  Finally, in the bottom right corner is the tan colored Grid/Generator transfer switch.